[image: image1.jpg]



PRIVATE AND CONFIDENTIAL

Author:  Robert Taylor

Date: 13th May 2009
_________________________________________________________________________________

_________________________________________________________________________


Pressure Ratings for Rubber Gaskets (all types)
Rubber materials are frequently chosen for gasket applications because of their unique physical characteristics.
The temperature and pressure limits for rubber gaskets are low compared to other gasket materials on the market.

Please see below table.

Rubber Type

	
	NR
	SBR
	EPDM
	NBR
	CR

	Max Temperature Deg C
	90
	100
	150
	130
	120

	Min Temperature Deg C
	-50
	-40
	-40
	-40
	-30

	Max Pressure (Bar)
	15
	16
	18
	18
	16


Due to the low pressure rating of a rubber gasket the flange selection is very important.
If the pressure rating of the flange is greater than the pressure limit of the gasket over compression of the gasket will occur, causing leakage of the gas or fluid being sealed.

Please see below table of recommended flange classes for the above rubber materials (DIN EN 1514)
	
	NR
	SBR
	EPDM
	NBR
	CR

	PN 6
	
	
	
	
	

	PN 10
	
	
	
	
	

	PN 16
	
	
	
	
	

	PN 40
	
	
	
	
	


Recommended
Not Recommended
These recommendations are for all nominal bore sizes.
1 of 1

